## COMPact Kiosk-type transformer station GRÄPER

## GBÜ-800 – continuous to 1x630 kVA

## Basic technical specifications:

- HV nominal voltage: 3 AC 22 kV 50 Hz

- LV nominal voltage: 3/PEN AC 420/242 V 50 Hz / TN-C,

- Frequency: 50 Hz

- Transformer nominal power: to 630 kVA

- HV bus-bars nominal current: cable input field 630 A, TR output field 200 A

- LV bus-bars nominal current:  to 1 000 A

- HV / LV distributor nominal insulation voltage: 24 kV / 1 000 V

- HV distributor short-time / dynamic current: 16 kA / 40 kA

- LV distributor short-time / dynamic current: to 30 kA / to 60 kA

- LV distributor cover: IP 65 / IP 20

- Whole station cover: IP 23D

- Cover class: K 20

- External dimensions (LxWxH): 2 500x2 200x2 470  mm

- Empty skeleton weight: cca 6 200 kg

- Environment: 3.1.1. basic (within the kiosk-type TS rooms),

4.1.1. external, ordinary (outside the TS rooms )

- Exposure class: for internal components: XC1; for external components: XC4, XF1, XA1.

- Operating conditions: ambient temperature –40°C ≤ t ≤ + 40°C

altitude up to 1 000 m asl.

Note: If the transformer substation is used in different climate and operating conditions, the TS supplier must be consulted.

Electrical current injury prevention:	(STN  EN 33 3201, STN EN 33 2000-4-41),

- in normal operation mode (of the live parts): in HV system by: 4.1.1 – out of reach placement

4.1.1 – live parts insulation

4.1.1 – barrier, cover

in LV system by:  3.7.1. live parts insulation

3.7.2. barriers or covers

3.8.5. out of reach placement (position)

– in case of failure (of dead parts): in HV system by: 4.2.5. automatic feed disconnection with quick IT networks disconnections to be off (with low imped. neutral TR grounding)

4.2.9. bonding – uniform potential installation

in LV system by:	  3.2.  automatic feed disconnection

3.6.1. additional protection by residual current              device (TS install.)

3.6.2. additional protection – additional protecting     bonding

Station construction:

# Externally controlled compact kiosk-type transformer substation is partially flush-mounted, with external dimensions of  2 500x2 200 mm, total height of 2 470 mm, clear height of the technological part is 2 100 mm, ground sinking depth of 750 mm, over ground height of 1 720 mm (with flat roof). The construction is self-supported and by default made of reinforced concrete Gräper LC 30/37, with 8/12 granularity. Steel reinforcement frame composed of steel bars and mats is bilaterally welded and conductively connected together and takes part in the bonding, grounding, or even lightning protection system. The installation of the station skeleton does not require any foundations, but only a well flushed and  rammed out cut. The transformer substation is type-approved, conforming to the STN EN 62271-202 norm and meets the resistance tests against internal arcing fault of the German  PEHLA directive.

Station construction is formed by a  compact unit consisting of two monolithic parts: basement tank with sidewalls and flat roof.

The basement tank and sidewall: Made of waterproof and oil proof concrete (crack width up to 0.2 mm guranteed) as an oil catch tank. The construction resistance against strong chemical influence of the liquids, soils and vapours conforms to DIN directive. The tank serves as a foundation for the non-freezing part and for lifting the whole station by means of 4 anchorage points (sealed chasing nuts) RD 36, placed in the shorter sides of the TS (as viewed on „B“, „D“). In order to join the external grounding, two М12 points of HV/LV switchgear are led out from the sidewalls of the station.The bell casting method was used to construct the tank and door frames, thus creating a monolithic unit which meets requirements for the impermeability of water and oil substances.

HV and LV cable entry holes are made on production  in the lower part of the body  (HV or LV distributor´s side). After cable installation, the entry holes are sealed by Hauff press fittings (4pcs HSI 150 D3/60 or 8pcs HSI90 D1/82). After installation, the cables are sealed against water penetration with default lids with corresponding number and diameter of cable entry necks (corresponding to cable type –), which are sealed by a closing lid with a thermal shrinking plastic sleeve. Optionally, the system lid can be fitted with a sleeve for sealing the cable protector (FXKV...) or thermal shrinking sleeve may by substituted by cold shrinking sleeves. Unoccupied inlets are sealed with system lid with bolt sealing and bayonet lock.

Optionally, an inlet for the side pass of a temporary construction outlet (e.g. Gräper system or Hauff-BD) may be installed in the LV distributor space.

The entry opening for  HV cables (cable space) is separated from the HV distributor with a steel plate. The distributor is placed on a steel construction including safety frame for the protection of  maintenance personnel and personal protection agains internal arcing fault according to PEHLA standards.

Internal walls are standardly treated with white washable paint. Surface finish of the outer walls is available in concretewith bare filler (exposed aggregate concrete) with 8/12 granularity. Other types of finish are available upon customer's demand.

Roof: The standard flat roof is fixed to the walls from inside at 4 points by screws and overlaps the  wall contour by 9 cm. It is possible to lift the wall by means of 4 anchorage points (sealed chasing nuts) RD 16, standardly corniced with width of 9 cm all around, thus the joints between vertical walls and roof are additionally protected. The roof can be lifted by  4 anchor points (sealed chasing nuts) RD 18.  In order to increase the protection of the concrete surface against humidity, the upper roof is covered with  additional hydrophobic coating, which fills capillary pores and  acts  against the hygroscopic properties of the concrete.

Surface finish of the roof can be made of exposed aggregate concrete, or fair-face concrete with rough surface and paint according to the RAL colour palette. The shape of the roof (flat, saddle) is optional as well.

Door: All  metal parts including doors, frames, and ventilating parts are made by default of hot-dip galvanized  1,5 mm thick sheet steel,  basic paint and two layers of the finish paint in RAL 7032 colour palette. The door is equipped with armour including external knob and internal handle with plastic lock cover and a pawl for fixing the door in  open position at a  95° angle. For arrestment – the locking, bob weights and point-to-point bars are used within each door wing frame (four- point locking system Gräper). The lock is adapted for standard lock inserts.  The outer side of the door is covered by warning plates in terms of the valid EN.

Optionally, the door and ventilating parts can be made of anodized aluminium and 2 lock inserts can be used  for double lockout.

# The access to the  HV and LV switchgear of the substation is provided by a common single wing door with full ventilation (slit shades Gräper with approved DIN 40 050 V2A safety level) with internal dimensions WxH of  1 110x1 428 mm, on the HV/LV transformer´s side there is a 2-wing door without ventilation (HV) and ventilation (LV) with internal dimensions WxH of 1 950x1 428mm. The door is equipped with an  arresting pawl for fixing in an open position and door wings are connected with the frame by  a copper conductor with 16 mm2 cross-section area.

Transformer air exchange calculation: Gräper GBÜ 800

- For  the Oil  transformer 22 kV, 630 kVA  Type : BEZ TOHn 378/22, „BA“

- Transformer strain in summer time: 50 % up to 60% of the nominal power

- Outside air temperature: +35 °C

- no-load losses: Po  = 1,3 kW

- load losses: Pkn = 8,4  kW

- Air vent  altitude difference: h = 1,6 m

- Calculation :

no-load losses: Po = 1,3 + 0,13  (10%)    = 1,43 kW

load losses: Pk =8,4  + 0,84(10%)     = 9,24 KW

N = 315 (50% of the nominal power)/630(100% of the nominal power) = 0,5

Total losses: Pz = Po + Pkn  x N² = 1,43 +9,24 x 0,25 = 3,74 kW

Heat losses for cooling calculation: Pch = 0,6 x Pz  = 0,6 x 3,74 = 2,244 kW

Ventilator diameter in m² :

- Air inlet:        Sp = 0,1942  x  (Pch/√h)  = 0,1942  x (2,244/√1,6) =    0,345  m²

- Air outlet:      So = 0,2007  x  (Pch/√h) = 0,2007 x   (2,244/√1,6) =      0,356  m²

Ventilators in  in transformer  station MKP 800 :

Air inlet: 1640 x 1410 mm²  = 2,3 m²  -  TS door

Air outlet  vent : 875  x  1350 mm² =  1,01 m² -  transformer space

Air exchange: Air vents for the transformer space are located in the entrance door  supplemented by a next fixed air vent in the opposite wall with internal dimensions (clearance)  WxH of 1 110x1428mm. The vents´ dimensions are designed to provide for a sufficient air ventilation and transformer cooling. Air vents are equipped with grid (lamellas) from outside and net against foreign bodies from inside.

Grounding:

Composition of the TS internal grounding:

- bonding bar (BB) Cu 30x4 mm with M12 clips, located on the spreader insulator 1 kV, which is directly connected with all the technological components of the TS (vessel of the TR distributors tanks of the HV, LV, metal shield of the HV cables, branch bar PEN) and with individual installed components (construction components  – tank and roof reinforcement, frames, door, grate, conducting „U“- beams of the transformer, bearing structures of the distributors...) using the Cu conductor with Smin 30 mm2. Each conductor of the grounding connected to the BB is labelled.

- earth artery implemented by strip conductor Fe with Smin 125 mm2, being part of the TS reinforcement and it is cast directly in the external walls and kiosk´s beam  which serves as the connection of the common points of the grounding. Flexible parts are connected to the  frame with copper (Cu) strip  or Cu grounding cable with min. cross-section area of 16 mm2.

- 2 nodes of the grounding feeder by Hauff HDE-M12/X to connect the external grounding (in general FeZn  stripe 30x4 mm) to the bonding bar (from the internal part of the node by a connecting screw M12-St 37 Zn, from  the external part of the node through test clips of the SZ1, SZ2 grounding with screw M12)

Transformer substation in the default finish does not have any external lightning system , as it is a ground object mostly located close to other higher objects. All the metal reinforcements cast in to the corresponding  part of the TS (roof, walls, false ceiling, basement tank) are welded into a single structure, using conductiveattachments (e.g. Cu lines 35 mm2). Reinforcements are welded together, thus creating a  Faraday´s cage and after the installation of the roof can be immediately connected to the grounding.  On customer demand, the transformer station can be equipped with  with external lightning rod with one collector in the middle of the roof and two leads connected to the common TS grounding via test clips in terms of the valid STN, EN.

For each transformer station  a common grounding system for HV and LV facilities must be constructed, its design needs to take into account the operating conditions – fault current value of the distribution network in the given region, power transformer node operation mode and local soil conditions (STN EN 33 3201, STN EN 33 2000-5-54, PNE 33 2000-1 )

# Installation:

# The internal installation of the station includes interior lighting of the TS, consisting of an oval incandescent 60 W lamp fitting with gate switch lighting in the distributor´s space of high and low voltage and  a  one-phase socket of 230 V. Circuits feeding the lighting and socket installation are led out of the main LV distributor via installation breakers or coupled with residual current device.

Further equipment – as specified by customer.

Internal TS space is divided into 3 compartments on the level of the basement tank: the transformer chamber, HV switchgear space and LV switchgear space. The TS over ground part comprises a single common space, divided by supporting constructions parts into the 3 separate compartments (one tranformer compartment and two distributor compartments).

# Transformer:

Oil, hermetic or dry-type transformers up to the power of  630 kVA may be used in the substation located on rails and  vibration absorbers made by Gräper. In case of  oil leakage the seat of the transformer is designed as an impermeable oil catch tank. If the transformer is equipped with bolster, it is fixed against side movement.Transformer insertion and removal can be performed through an entrance door or by crane if roof  is removed. Max. dimensions of the TR  (LxWxH) are cca 1 750x850x1800 mm.

Transformer cooling is atmospheric. Air renewal is provided by air vents in the door of the transformer substation (on the transformer´s side ) and through an air vent.

The  protection of the transformer against over current, or shortcut is provided:

a) on HV side – by plugs or by switch with safety relay IEC  60 281-1,

b) on LV side – by air breaker with electronic trigger.

High voltage distributor:

In transformer substation it is possible to use all the types of the commonly produced covered HV gas insulated distributors SF6 (for example GA, GA-C by Moeller, 8DJ10, 8DJ20 by Siemens, RM6 by Merlin Gerin,...), or type-approved vacuum  distributors up to the width of 3 fields. Depending on the type used the nominal current of the distributors can be up to 630 A, shorting resistance (nominal short-time withstand current 1 s) up to 20 kA, optionally up to 25 kA. The HV distributor may be delivered by the customer  or by Gräper company,  including the zinc-coated supporting construction and  a construction for decreasing  pressure in the arcing fault in the HV distributor conforming to   PEHLA standards. Max. dimensions of the HV distributor are ca: 1760x1 400x775 mm.

- Bus-bars nominal current – cable entry field  630 A

- cable departure field TR 200 A

- switchgear nominal short-term current: 16 kA

- switchgear nominal dynamic current:  40 kA

- Cover: IP 65

# Optionally, this transformer station may be used in setup No. 1 combined with electricity consumption measurement on the HV side in the transformer station: 8DJ20.10 (2RK+1T) + 8DH10.ME1-K. Switchgear size: cca 1910x1 400x775 mm

# Low voltage distributor:

The panel version of the LV distributor is covered with IP 20. The feeder is equipped with air breaker depending  on the transformer´s power,  breakage bar switches  are inserted (12-13 outlets with switches to 400 A and construction width of 100 mm for one TR, or corresponding number of outlets with switches to 160 A and construction width of 50 mm), or breakers with max. attachable cable section of 300 mm2. Standard nominal current of the distributor can be up to 1 000 A, shorting resistance (short-time nominal withstand current 1 s) to 25 kA. Besides this, the distributor can include electricity consumption monitor, circuits for station lighting and service socket. The clips can be grounded on the main breaker´s feeder („ball pivots“)  25 mm, which allow to protect the work place during maintenance of the LV distributor via grounding tool (shorting set). Max. dimensions of the LV distributor (WxLxH) are cca: 1 100x1 400x350 mm.

Note: The number of LV outlets is limited by customer´s demands for LV distributor to be equipped with further devices for measurement, etc.

The distributors meet STN EN 60439-1 norm and also DIN VDE 0660, part 500, VDE 0100, VDE 0414, UVV standard requirements.

Cable connections:

Cable connections include HV distributor connection with transformer 24 kV by single-core cables 24-N2XSY 3x1x35 mm2 and LV distributor connection with transformer 1 kV by cables 1-NYY-O 1x150 mm2, resp. 1x240 mm2.

Cable connections for high voltage are checked in each production phase. Filed tests of the TE fractional discharges in Gräper company´s own test-room can be carried out , following VDE 0434, VDE 0472 technical norms. According to the regulations the maximum allowed value for  TE is ≤ 20pC. The real achieved value is ≤ 5 pC

Transformer  station construction  specifications:

The station is constructed according to the norms and rules of STN EN, DIN, UVV etc., directly following the bellow given  normative standards:

Cellular concrete 				- DIN 4219

Armoured concrete 				- DIN 1045

Directives VDE					- DIN 0141, 0101, 0100

Directive on the protection of underground 	- GwSchV

Federal directive on waste disposal		- BimSchV

Electromagnetic radiation compliance		- BimSchV č.26

Individual structural components of the transformer substation are made of uninflammable materials, fire resistance of the station construction meets STN 73 0821 norms (fire resistance class required is F90, class documented is F120).

# Delivery, assembly,  ground cut for  station placement:

# The kiosk-type transformer station is delivered assembled and prepared for HV, LV cable connection and grounding. It is installed by  crane into a prepared  pit with  compressed and flat surface according to the design project of the transformer substation´s producer  – Gräper company (dimensions of the ground cut: 310x280 cm, cutting depth: 95 cm, compressed layer thickness: min. 20 cm).